## Material compatibility table
KEY
WET PARTS EXECUTIONS
MEDIUM | B | B33 | B56 | B2 | A | F | V | A+ | EXCELLENT
[8 empty] | A | VERY GOOD
Acetic acid (peracetic) | C | C | B | C | A | B | C | B | GOOD
Citric acid | B | B | B | B | A | B | C | C | NOT SUGGESTED
Hydrochloric acid - HCl | A | D | D | A+ | D | A+ | A | D | DAMAGE
Sulfuric acid - H2SO4 diluited | B | D | D | B | D | B | A | LOW N° OF STROKES (34-71)
Sulfuric acid - H2SO4 96÷98% | B | C | A | A | C | A+ | B
Alcool | B | B | C | B | A | B | C
Sodium aluminum 52 | B | C | B | A | D | B | B
Ammonia | A | B | B | B | D | B | B
Sulfur dioxide - SO2 | B | C | A | A | D | B | B
Antiscalant | C | B | B | C | A | C | C
Biocide | B | C | C | A | D | B | B
Activated charcoal | C | B | A | C | A | C | C
Sodium chlorite - NaClO2 | D | D | D | A | D | A+ | D
Chlorine | A | D | C | A | D | B | B
Aluminum chloride | B | C | B | A | D | A+ | B
Ferric chloride - FeCl3 | A | D | D | A | D | A+ | A
Coagulant | A | C | C | A | D | B | B
Detergent | A | B | B | B | A | C | B
Flocculant | B | B | C | A | A | C | B
Fluoride | C | D | C | A+ | D | C | C
Trisodium phosphate | B | C | C | C | A | C | C
Hydrogen peroxide - H2O2 | C | B | B | C | A | C | B
Calcium hypochlorite | B | D | C | A | D | A+ | B
Sodium hypochlorite - NaOCl | B | D | D | A | D | A+ | A
Lime | C | B | A | C | A | A+ | B
Aluminum polychloride (PAC) | B | B | A | A | B | A+ | B
Polyelectrolyte | C | B | B | C | A | C | B
Polymer | A | B | C | C | A | C | B
Anionic polymer | C | B | C | C | A | C | B
Cationic polymer | C | B | C | C | A | C | B
Sodium hydroxide - NaOH | B | A | A | A | A | A+ | B
Aluminum sulphate | B | B | A | B | D | A+ | B
Copper sulfate | A | C | C | B | D |  | B
Ferric sulphate ≤ 10% | B | B | A | A | D | A+ | B
Ferrous sulphate | B | A | A | A | D | A+ | B
Trisodium solfate | D | C | C | C | D | A+ | B
Sodium solfite | B | C | C | A | D | A | A
Solvent | B | C | B | A | A | B | D
Paint | A | A | B | B | A | B | C